Indoor / Outdoor Long-term Model

Online Type Stability Voltage Uninterruptible Power System

12VDC Powered Distance Voltage Drop Test Report

| No. | Battery Voltage | Test conditions |  |  |  | Distance |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Transformers No Power Supply | Transformers Power Supply | Camera No Power Supply | Camera Power Supply | 1.5M | 47M 1.5+45 +0.5=47 | 55M 1.5+45 +1.5*5+1=55 | 63M 1.5+45 +1.5*10+1.5=63 | 71M 1.5+45 +1.5*15+2=71 |
| Measuring Voltage | 13.3V | ▓ |  | ▓ |  | 13.3V | 13.3V | 13.29V | 13.29V | 13.28V |
| DC voltage difference distance less than the AC voltage difference from many (Consistent with the theory of electricity) |  |  |  |  |  |  |  |  |  |  |
| Measuring Voltage | 13.2V | ▓ |  |  | ▓ | 13.05V | 12.44V | 12.12V | 11.74V | 11.46V |
| Camera Operation |  |  |  |  |  | OK | OK | OK | OK | OK |
| Thread number not included in voltage reduction assessments |  |  |  |  |  |  |  |  |  |  |
| Measuring Voltage | 13.2V |  | ▓ |  | ▓ | 13.06V | 12.5V | 12.23V | 11.9V | 11.52V |
| Camera Operation |  |  |  |  |  | OK | OK | OK | OK | OK |
| Recommended 1:12VDC power supply within distance to 50M is good. Recommended 2 distance after over 50M: 12VDC power supply, voltage after voltage drop is less than 12.3V, but because most of the cameras are operating within the range of 9V~16V, therefore can also be functioning properly. |  |  |  |  |  |  |  |  |  |  |